## system input output
Hemmes Energietechniek |  | DHV Projectmanagement
program version L1.16 E march 2004
Conditioning the air in pools, spa's and other humid areas with different types of Air Handling Units (AHU)
Save this file under another name before changing values
Due to iteration there is a possibility that you get #num in the cells (not stable enough): start again with another copy of the original
The iteration prefers a gradual change of fresh air temperature using the button
The indication "condens" means that the air condition has reached the saturation line
doesn't work yet
General data | [12 empty] | FALSE
[6 empty] | efficiency of E-production | 0.4
atmospheric air pressure | 1.013 | bar |  |  | powerplant
return air condition | 31 | 51 | oC % |  |  | efficiency of heat production | 0.9 |  |  | doesn't work yet
outside (fresh) air condition | 20 | 70 | oC % |  | local | [7 empty] | FALSE
Hemmes system |  |  |  | recirculating system |  |  |  | ventilating fresh air |  |  |  | ventilating drier fresh air
drying the fresh air |  |  |  | drying the return air |  |  |  | no active drying in AHU |  |  |  | drying the fresh air
+ heatrecovery from return air
dehumidification before heatregain
Supply air massflow | 1000 | kg/h |  |  | 1000 | kg/h |  |  | 1000 | kg/h |  |  | 1000 | kg/h
this is an airflow of | 864.8223 | m3/h |  |  | 864.8223 | m3/h |  |  | 867.2865 | m3/h |  |  | 864.8223 | m3/h
dehumidification | 8.9335 | kg/h |  |  | 8.9335 | kg/h |  |  | 4.1511 | kg/h |  |  | 8.9335 | kg/h
thermal efficiency of heatexchanger in dry-loop | 60 | % |  |  | 60 | % | [6 empty] | 60 | %
th.efficiency of heatexchanging with return air | 60 | % | [6 empty] | 60 | %
in the dehum.section air is cooled down to | 5 | oC | condens |  | 5 | oC | condens | [5 empty] | 5 | oC | condens
the stale air is further cooled down to | 12 | oC | condens | [5 empty] | 12 | oC | condens
before this cooler the stale air was | 20.966 | oC | [6 empty] | 24.4504 | oC
after the heatexchanger(s) supply air temp is | 24.2 | oC |  |  | 20.6 | oC |  |  | 26.6 | oC |  |  | 14 | oC
warming it up to same temp as return air | 31 | oC |  |  | 31 | oC |  |  | 31 | oC |  |  | 31 | oC
warming it up to desired setpoint of supply air | 31 | oC |  |  | 31 | oC |  |  | 31 | oC |  |  | 31 | oC
Cooling capacity in dehumidifier section | -5.0651 | kW |  |  | -9.2849 | kW | [6 empty] | -5.0651 | kW
Cooling capacity in stale air cooler | -6.5099 | kW | [6 empty] | -7.5092 | kW |  | is possible but not applied here
Heating the supply up to return air temp takes | 1.9212 | kW |  |  | 2.938 | kW |  |  | 1.254 | kW |  |  | 4.8018 | kW
Further to the supply air temp setpoint takes | 0 | kW |  |  | 0 | kW |  |  | 0 | kW |  |  | 0 | kW
|  | has to do | can do |  |  | has to do |  |  |  | has to do | can do |  |  | has to do | can do
Heatpump function | cold kW | -5.0651 | -11.5749 |  | cold kW | -9.2849 |  |  | cold kW | 0.01 | -7.5092 |  | cold kW | -5.0651 | -5.0651
| COPcooling | 3 | 3 |  | COPcooling | 3 |  |  | COPcooling | 3 | 3 |  | COPcooling | 3 | 3
| E-power | 1.6884 | 3.8583 |  | E-power | 3.095 |  |  | E-power | 0.0033333 | 2.5031 |  | E-power | 1.6884 | 1.6884
| heat prod. | 6.7534 | 15.4333 |  | heat prod. | 12.3799 |  |  | heat prod. | 0.013333 | 10.0123 |  | heat prod. | 6.7534 | 6.7534
heat required to bring it to return air temp | necessary | 1.9212 | 1.9212 |  | necess. | 2.938 |  |  | necessary | 1.254 | 1.254 |  | necessary | 4.8018 | 4.8018
Useful heat production (kW) |  | 4.8323 | 13.5121 |  |  | 9.4419 |  |  |  | -1.2407 | 8.7583 |  |  | 1.9516 | 1.9516
Heatpumpfactor (kWheat per kW e-power) |  | 2.8621 | 3.5021 |  |  | 3.0507 |  |  |  |  | 3.499 |  |  | 1.1559 | 1.1559
(the higher the better)
Primary energy use (negative is heat production) |  | -1.1483 | -5.3677 |  |  | -2.7536 |  |  |  | 1.3868 | -3.4738 |  |  | 2.0524 | 2.0524
(more negative is better)
Primary energy use per dehumidified kilo of water |  | -0.12854 | -0.60084 |  |  | -0.30823 |  |  |  | 0.33409 | -0.83682 |  |  | 0.22975 | 0.22975
(more negative is better)
Another factor combining also air flow and dehum cap. |  | -3.2865 | -18.7979 |  |  | -8.4004 |  |  |  | 0 | -12.1547 |  |  | 2.3725 | 2.3725
(more negative is better)
All this without the influence of the change in COP at different temperatures (lower COP at lower temperatures)
All this without the influency of the Electrical power input for the fans
Hemmes cools deeper and thus a lower COP and more power input for compressor but less air is needed and this reduces fan power input
| Example AHU |  |  | Example AHU |  |  |  |  | Example AHU |  |  |  | Example AHU
|  |  |  | Menerga thermocond 37WPR |  |  |  | Menerga thermocond 37WPR |  |  |  | Menerga thermocond 37WPR option
| New Hemmes concept |  |  | and most stand alone dehumidifiers |  |  |  | most AHU's (but without stale air cooler) |  |  |  | New since jan 2004
Note on C53: hemmes:
set same dehumidification capacity
set same airflow

## hemmes ventilerend (hidden)
Hemmes systeem
ontvochtigen vóór warmteterugwinning
datum 13 mrt 2004
| flow | 1000 | kg/hr | flow inblaas | 864.8223 | m3/h
| luchtdruk | 1.013 | bar
| rendement 1 | 60 | % | ontvochtiging | 8.9335 | kg/h
| rendement 2 | 60 | %
|  | BL | [11 empty] | Toevoer | retour | [10 empty] | afblaas
|  | Ontvochtigen van de buitenlucht | [8 empty] | Hemmes systeem 2e warmtewisselaar
[16 empty] | werkt niet | [9 empty] | nakoelen
|  | aanzuig | dauwpunt | voor verd | afblaas | werkelijke afbl | gekoeld | uitwtw |  |  |  | toevoer | naverw | naverw | retour | retour bev | dauwpunt | afblaas | afblaas | werkelijke afbl | in koeler | dauwpunt | in koeler | langs | werkelijk | werkelijk
|  | t1 |  | geen 100% | verz.lijn | t2 | t3 | t4 |  |  | t5 | t6 | t6a | t6b |  | t7 |  | geen 100% | verz.lijn | t8 |  |  | geen 100% | verz.lijn |  | t9
celsius | t | 20 | 14.3485 | 11.0793 | 13.085 | 13.085 | 5 | 14 |  |  | 14 | 24.2 | 31 | 31 | 31 | 31 | 19.6528 | 20.966 | 20.056 | 20.966 | 20.966 | 19.6528 | -1.7248 | 11.9988 | 11.9988 | 12
bar | pd | 0.023316 | 0.016321 | 0.01318 | 0.015036 | 0.015036 | 0.0087266 | 0.015956 |  |  | 0.015956 | 0.030097 | 0.044746 | 0.044746 | 0.044746 | 0.044746 | 0.02282 | 0.024744 | 0.023396 | 0.024744 | 0.024744 | 0.02282 | 0.0052875 | 0.014004 | 0.014004 | 0.014005
% | RV | 70% | 100% | 123.8% | 100% | 100% | 100% | 54.69% |  |  | 54.69% | 29% | 19.5% | 19.5% | 51% | 51% | 100% | 92.23% | 100% | 92.23% | 92.23% | 100% | 431.6% | 100% | 100% | 100%
kg/kg | x | 0.010189 | 0.010189 | 0.010189 | 0.0093748 | 0.0093748 | 0.0054069 | 0.0054069 |  |  | 0.0054069 | 0.0054069 | 0.0054069 | 0.0054069 | 0.01434 | 0.01434 | 0.01434 | 0.01434 | 0.014711 | 0.01434 | 0.01434 | 0.01434 | 0.01434 | 0.0087225 | 0.0087225 | 0.0087232
[5 empty] | 36.835 | [13 empty] | 57.513 |  |  |  |  | 34.0775
kJ/kg | h | 45.9821 | 40.1867 | 36.835 | 36.835 | 36.835 | 18.6007 | 27.7479 |  |  | 27.7479 | 38.1183 | 45.0345 | 45.0345 | 67.8834 | 67.8834 | 56.1562 | 57.513 | 57.513 | 57.513 | 57.513 | 56.1562 | 34.0775 | 34.0775 | 34.0775 | 34.0775
kg/hr | massaflow | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 |  |  | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
m3/hr | volumeflow | 844.4373 | 828.1579 | 818.7406 | 823.4563 | 823.4563 | 795.17 | 820.899 |  |  | 820.899 | 850.0586 | 869.4983 | 869.4983 | 881.8743 | 881.8743 | 848.9734 | 852.781 | 843.2156 | 852.781 | 852.781 | 848.9734 | 786.9897 | 815.2046 | 819.4842 | 819.4886
kW | vermogen |  |  |  |  | -2.5409 | -5.0651 | 2.5409 |  |  |  | 2.8807 | 1.9212 | 0 | [5 empty] | -2.8807 | [5 empty] | -6.5099
kg/hr | ontvochtig |  |  |  |  | -0.81454 | -3.9679 |  | -4.7824 | kg/hr ontvochtiging | [9 empty] | 0 | [5 empty] | -5.6172
| t hulp |  | 14.3485 |  | 13.085 | [11 empty] | 19.6528 |  | 20.056 |  |  | 19.6528 |  | 11.9988
xoud
h oud
| pd oud |  | 0.016319 |  | 0.015036 | [11 empty] | 0.02282 |  | 0.023396 |  |  | 0.02282 |  | 0.014004
| cpl | 1.0064 | 1.0063 | 1.0063 | 1.0063 | 1.0063 | 1.0062 | 1.0063 |  |  | 1.0063 | 1.0065 | 1.0066 | 1.0066 | 1.0066 | 1.0066 | 1.0064 | 1.0064 | 1.0064 | 1.0064 | 1.0064 | 1.0064 | 1.0061 | 1.0063 | 1.0063 | 1.0063
| cpd | 1.8414 | 1.8401 | 1.8394 | 1.8398 | 1.8398 | 1.838 | 1.84 |  |  | 1.84 | 1.8424 | 1.8439 | 1.8439 | 1.8439 | 1.8439 | 1.8413 | 1.8416 | 1.8414 | 1.8416 | 1.8416 | 1.8413 | 1.8365 | 1.8396 | 1.8396 | 1.8396
pd
hw
| ro | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 |  |  | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.15
hds
hdnat
xs
| rho | 1.1963 | 1.2198 | 1.2338 | 1.2258 | 1.2258 | 1.2644 | 1.2248 |  |  | 1.2248 | 1.1828 | 1.1563 | 1.1563 | 1.1502 | 1.1502 | 1.1948 | 1.1895 | 1.2034 | 1.1895 | 1.1895 | 1.1948 | 1.2889 | 1.2374 | 1.2309 | 1.2309
uit zeller boekje pagina 3
| temp celsius | 20 | 14.3483 | 11.0793 | 13.085 | 13.085 | 5 | 14 |  |  | 14 | 24.2 | 31 | 31 | 31 | 31 | 19.6528 | 20.966 | 20.056 | 20.966 | 20.966 | 19.6528 | -1.7248 | 11.9988 | 11.9988 | 12
spec warmtecapaciteit droge lucht | cpl | 1.0064 | 1.0063 | 1.0063 | 1.0063 | 1.0063 | 1.0062 | 1.0063 |  |  | 1.0063 | 1.0065 | 1.0066 | 1.0066 | 1.0066 | 1.0066 | 1.0064 | 1.0064 | 1.0064 | 1.0064 | 1.0064 | 1.0064 | 1.0061 | 1.0063 | 1.0063 | 1.0063
spec warmtecapaciteit waterdamp | cpd | 1.8414 | 1.8401 | 1.8394 | 1.8398 | 1.8398 | 1.838 | 1.84 |  |  | 1.84 | 1.8424 | 1.8439 | 1.8439 | 1.8439 | 1.8439 | 1.8413 | 1.8416 | 1.8414 | 1.8416 | 1.8416 | 1.8413 | 1.8365 | 1.8396 | 1.8396 | 1.8396
dampdruk waterdamp | pd | 0.023316 | 0.016319 | 0.01318 | 0.015036 | 0.015036 | 0.0087266 | 0.015956 |  |  | 0.015956 | 0.030097 | 0.044746 | 0.044746 | 0.044746 | 0.044746 | 0.02282 | 0.024744 | 0.023396 | 0.024744 | 0.024744 | 0.02282 | 0.0052875 | 0.014004 | 0.014004 | 0.014005
| T | 293.15 | 287.4983 | 284.2293 | 286.235 | 286.235 | 278.15 | 287.15 |  |  | 287.15 | 297.35 | 304.15 | 304.15 | 304.15 | 304.15 | 292.8028 | 294.116 | 293.206 | 294.116 | 294.116 | 292.8028 | 271.4252 | 285.1488 | 285.1488 | 285.15
| T2 | 85936.9225 | 82655.2716 | 80786.272 | 81930.4719 | 81930.472 | 77367.4225 | 82455.1225 |  |  | 82455.1225 | 88417.0225 | 92507.2225 | 92507.2225 | 92507.2225 | 92507.2225 | 85733.4809 | 86504.2229 | 85969.7496 | 86504.2229 | 86504.2229 | 85733.4809 | 73671.655 | 81309.8229 | 81309.8229 | 81310.5225
| A | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 |  |  | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151
| B | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 |  |  | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726
| c | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 |  |  | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625
| teta | 0.0018368 | 0.0018862 | 0.0019157 | 0.0018975 | 0.0018975 | 0.0019728 | 0.0018893 |  |  | 0.0018893 | 0.0018015 | 0.0017467 | 0.0017467 | 0.0017467 | 0.0017467 | 0.0018398 | 0.0018286 | 0.0018363 | 0.0018286 | 0.0018286 | 0.0018398 | 0.0020392 | 0.0019073 | 0.0019073 | 0.0019073
| D | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 |  |  | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42
| E | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 |  |  | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414
| F | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 |  |  | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979
| <0 tau | -1.5411 | -1.7218 | -1.8296 | -1.7631 | -1.7631 | -2.0368 | -1.7331 |  |  | -1.7331 | -1.4113 | -1.2089 | -1.2089 | -1.2089 | -1.2089 | -1.552 | -1.5109 | -1.5393 | -1.5109 | -1.5109 | -1.552 | -2.2768 | -1.799 | -1.799 | -1.7989
| 10^ | 0.028768 | 0.018978 | 0.014806 | 0.017254 | 0.017254 | 0.0091883 | 0.018488 |  |  | 0.018488 | 0.038786 | 0.061811 | 0.061811 | 0.061811 | 0.061811 | 0.028055 | 0.030838 | 0.028884 | 0.030838 | 0.030838 | 0.028055 | 0.0052875 | 0.015886 | 0.015886 | 0.015888
| G | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 |  |  | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047
| H | -3177 | -3177 | -3177 | -3177 | -3177 | -3177 | -3177 |  |  | -3177 | -3177 | -3177 | -3177 | -3177 | -3177 | -3177 | -3177 | -3177 | -3177 | -3177 | -3177 | -3177 | -3177 | -3177 | -3177
| K | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 |  |  | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703
| >0 tau | -1.6324 | -1.7873 | -1.8801 | -1.8229 | -1.8229 | -2.0592 | -1.7971 |  |  | -1.7971 | -1.5215 | -1.3492 | -1.3492 | -1.3492 | -1.3492 | -1.6417 | -1.6065 | -1.6309 | -1.6065 | -1.6065 | -1.6417 | -2.2677 | -1.8538 | -1.8538 | -1.8537
| 10^ | 0.023316 | 0.016319 | 0.01318 | 0.015036 | 0.015036 | 0.0087266 | 0.015956 |  |  | 0.015956 | 0.030097 | 0.044746 | 0.044746 | 0.044746 | 0.044746 | 0.02282 | 0.024744 | 0.023396 | 0.024744 | 0.024744 | 0.02282 | 0.0053986 | 0.014004 | 0.014004 | 0.014005
enthalpie van water | hw | 83.0652 | 59.6003 | 46.0603 | 54.3648 | 54.3648 | 20.9517 | 58.1565 |  |  | 58.1565 | 100.5449 | 128.9118 | 128.9118 | 128.9118 | 128.9118 | 81.6218 | 87.0826 | 83.298 | 87.0826 | 87.0826 | 81.6218 | -6.7027 | 49.8663 | 49.8663 | 49.8713
verdampingswarmte van waterdamp | r | 2453.9877 | 2467.1999 | 2474.7994 | 2470.1404 | 2470.1404 | 2488.8492 | 2468.0111 |  |  | 2468.0111 | 2444.1084 | 2428.0018 | 2428.0018 | 2428.0018 | 2428.0018 | 2454.8021 | 2451.7201 | 2453.8564 | 2451.7201 | 2451.7201 | 2454.8021 | 2504.2653 | 2472.665 | 2472.665 | 2472.6621
enthalpie van waterdamp op verz.lijn | hd | 2537.0529 | 2526.8001 | 2520.8598 | 2524.5052 | 2524.5052 | 2509.8009 | 2526.1675 |  |  | 2526.1675 | 2544.6533 | 2556.9136 | 2556.9136 | 2556.9136 | 2556.9136 | 2536.4239 | 2538.8026 | 2537.1544 | 2538.8026 | 2538.8026 | 2536.4239 | 2497.5626 | 2522.5313 | 2522.5313 | 2522.5335
xd
enthalpie van waterdamp in het natdampgebied | hd | 83.0652 | 59.6003 | 46.0603 | 54.3648 | 54.3648 | 20.9517 | 58.1565 |  |  | 58.1565 | 100.5449 | 128.9118 | 128.9118 | 128.9118 | 128.9118 | 81.6218 | 87.0826 | 83.298 | 87.0826 | 87.0826 | 81.6218 | -6.7027 | 49.8663 | 49.8663 | 49.8713
1
2
3
4
5
7
6
8
6a
6b
9

## recirculerend (hidden)
Recirculerend systeem
zoals Menerga in ruststand of Dantherm, GEA
datum 13mrt 2004
| flow | 1000 | kg/hr | flow inblaas | 864.8223 | m3/h
| luchtdruk | 1.013 | bar
| rendement 1 | 60 | % | ontvochtiging | 8.9335 | kg/h
| rendement 2 | 0 | %
|  | Ontvochtigen retourlucht | [8 empty] | Tweede warmtewisselaar met rendement =0
werkt niet
|  | aanzuig | dauwpunt | voor verd | afblaas | werkelijke afbl | gekoeld | uitwtw |  |  |  | toevoer | naverw | naverw | retour | retour bev
|  | t1 |  | geen 100% | verz.lijn | t2 | t3 | t4 |  |  | t5 | t6 | t6a | t6b |  | t7
celsius | t | 31 | 19.6528 | 15.6555 | 18.3837 | 18.3837 | 5 | 20.6 |  |  | 20.6 | 20.6 | 31 | 31 | 31 | 31
bar | pd | 0.044746 | 0.02282 | 0.017748 | 0.021087 | 0.021087 | 0.0087266 | 0.024194 |  |  | 0.024194 | 0.024194 | 0.044746 | 0.044746 | 0.044746 | 0.044746
% | RV | 51% | 100% | 128.6% | 100% | 100% | 100% | 36.07% |  |  | 36.07% | 36.07% | 19.5% | 19.5% | 51% | 51%
kg/kg | x | 0.01434 | 0.01434 | 0.01434 | 0.013228 | 0.013228 | 0.0054069 | 0.0054069 |  |  | 0.0054069 | 0.0054069 | 0.0054069 | 0.0054069 | 0.01434 | 0.01434
52.0265
kJ/kg | h | 67.8834 | 56.1562 | 52.0265 | 52.0265 | 52.0265 | 18.6007 | 34.4576 |  |  | 34.4576 | 34.4576 | 45.0345 | 45.0345 | 67.8834 | 67.8834
kg/hr | massaflow | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 |  |  | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
m3/hr | volumeflow | 881.8743 | 848.9734 | 837.3834 | 843.817 | 843.817 | 795.17 | 839.767 |  |  | 839.767 | 839.767 | 869.4983 | 869.4983 | 881.8743 | 881.8743
kW | vermogen |  |  |  |  | -4.4047 | -9.2849 | 4.4047 |  |  |  | 0 | 2.938 | 0
kg/hr | ontvochtig |  |  |  |  | -1.1121 | -7.8214 |  | -8.9335 | kg/hr ontvochtiging
| t hulp |  | 19.6528 |  | 18.3837
xoud
h oud
| pd oud |  | 0.02282 |  | 0.021087
| cpl | 1.0066 | 1.0064 | 1.0064 | 1.0064 | 1.0064 | 1.0062 | 1.0064 |  |  | 1.0064 | 1.0064 | 1.0066 | 1.0066 | 1.0066 | 1.0066
| cpd | 1.8439 | 1.8413 | 1.8404 | 1.841 | 1.841 | 1.838 | 1.8415 |  |  | 1.8415 | 1.8415 | 1.8439 | 1.8439 | 1.8439 | 1.8439
pd
hw
| ro | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 |  |  | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5
hds
hdnat
xs
| rho | 1.1502 | 1.1948 | 1.2113 | 1.2008 | 1.2008 | 1.2644 | 1.1972 |  |  | 1.1972 | 1.1972 | 1.1563 | 1.1563 | 1.1502 | 1.1502
uit zeller boekje pagina 3
| temp celsius | 31 | 19.6528 | 15.6555 | 18.3837 | 18.3837 | 5 | 20.6 |  |  | 20.6 | 20.6 | 31 | 31 | 31 | 31
spec warmtecapaciteit droge lucht | cpl | 1.0066 | 1.0064 | 1.0064 | 1.0064 | 1.0064 | 1.0062 | 1.0064 |  |  | 1.0064 | 1.0064 | 1.0066 | 1.0066 | 1.0066 | 1.0066
spec warmtecapaciteit waterdamp | cpd | 1.8439 | 1.8413 | 1.8404 | 1.841 | 1.841 | 1.838 | 1.8415 |  |  | 1.8415 | 1.8415 | 1.8439 | 1.8439 | 1.8439 | 1.8439
dampdruk waterdamp | pd | 0.044746 | 0.02282 | 0.017748 | 0.021087 | 0.021087 | 0.0087266 | 0.024194 |  |  | 0.024194 | 0.024194 | 0.044746 | 0.044746 | 0.044746 | 0.044746
| T | 304.15 | 292.8028 | 288.8055 | 291.5337 | 291.5337 | 278.15 | 293.75 |  |  | 293.75 | 293.75 | 304.15 | 304.15 | 304.15 | 304.15
| T2 | 92507.2225 | 85733.4809 | 83408.6378 | 84991.9258 | 84991.9258 | 77367.4225 | 86289.0625 |  |  | 86289.0625 | 86289.0625 | 92507.2225 | 92507.2225 | 92507.2225 | 92507.2225
| A | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 |  |  | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151
| B | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 |  |  | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726
| c | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 |  |  | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625
| teta | 0.0017467 | 0.0018398 | 0.0018746 | 0.0018507 | 0.0018507 | 0.0019728 | 0.0018317 |  |  | 0.0018317 | 0.0018317 | 0.0017467 | 0.0017467 | 0.0017467 | 0.0017467
| D | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 |  |  | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42
| E | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 |  |  | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414
| F | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 |  |  | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979
| <0 tau | -1.2089 | -1.552 | -1.6793 | -1.592 | -1.592 | -2.0368 | -1.5223 |  |  | -1.5223 | -1.5223 | -1.2089 | -1.2089 | -1.2089 | -1.2089
| 10^ | 0.061811 | 0.028055 | 0.020925 | 0.025584 | 0.025584 | 0.0091883 | 0.030038 |  |  | 0.030038 | 0.030038 | 0.061811 | 0.061811 | 0.061811 | 0.061811
| G | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 |  |  | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047
| H | -3177 | -3177 | -3177 | -3177 | -3177 | -3177 | -3177 |  |  | -3177 | -3177 | -3177 | -3177 | -3177 | -3177
| K | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 |  |  | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703
| >0 tau | -1.3492 | -1.6417 | -1.7509 | -1.676 | -1.676 | -2.0592 | -1.6163 |  |  | -1.6163 | -1.6163 | -1.3492 | -1.3492 | -1.3492 | -1.3492
| 10^ | 0.044746 | 0.02282 | 0.017748 | 0.021087 | 0.021087 | 0.0087266 | 0.024194 |  |  | 0.024194 | 0.024194 | 0.044746 | 0.044746 | 0.044746 | 0.044746
enthalpie van water | hw | 128.9118 | 81.6218 | 65.0216 | 76.3479 | 76.3479 | 20.9517 | 85.5602 |  |  | 85.5602 | 85.5602 | 128.9118 | 128.9118 | 128.9118 | 128.9118
verdampingswarmte van waterdamp | r | 2428.0018 | 2454.8021 | 2464.1522 | 2457.7756 | 2457.7756 | 2488.8492 | 2452.5796 |  |  | 2452.5796 | 2452.5796 | 2428.0018 | 2428.0018 | 2428.0018 | 2428.0018
enthalpie van waterdamp op verz.lijn | hd | 2556.9136 | 2536.4239 | 2529.1738 | 2534.1235 | 2534.1235 | 2509.8009 | 2538.1398 |  |  | 2538.1398 | 2538.1398 | 2556.9136 | 2556.9136 | 2556.9136 | 2556.9136
xd
enthalpie van waterdamp in het natdampgebied | hd | 128.9118 | 81.6218 | 65.0216 | 76.3479 | 76.3479 | 20.9517 | 85.5602 |  |  | 85.5602 | 85.5602 | 128.9118 | 128.9118 | 128.9118 | 128.9118
1
2
3
4
5
7
6
8
6a
6b
9

## ventilerend (hidden)
Ventilerend systeem met warmtewisselaar en afblaaskoeler
bijvoorbeeld Menerga wpr37 en DanthermX
datum 13mrt 2004
| flow | 1000 | kg/hr | flow inblaas | 867.2865 | m3/h
| luchtdruk | 1.013 | bar
| rendement 1 | 0 | % | ontvochtiging | 4.1511 | kg/h
| rendement 2 | 60 | %
|  | Ontvochtigen van de buitenlucht wordt niet toegepast | [8 empty] | Hemmes systeem 2e warmtewisselaar
[7 empty] | niet | [8 empty] | werkt niet | [10 empty] | nakoelen
|  | aanzuig | dauwpunt | voor verd | afblaas | werkelijke afbl | gekoeld | uitwtw |  |  |  | toevoer | naverw | naverw | retour | retour bev | dauwpunt | voor verd | afblaas | werkelijke afbl |  | in koeler | dauwpunt | afblaas | afblaas | werkelijke afbl | werkelijk
|  | t1 |  | geen 100% | verz.lijn | t2 | t3 | t4 |  |  | t5 | t6 | t6a | t6b |  | t7 |  | geen 100% | verz.lijn | t8 |  |  |  | geen 100% | verz.lijn | t8 | t9
celsius | t | 20 | 14.3485 | 20 | 16.4029 | 20 | 20 | 20 |  |  | 20 | 26.6 | 31 | 31 | 31 | 31 | 19.6528 | 24.4504 | 21.0948 | 24.4504 |  | 24.4504 | 19.6528 | -1.7218 | 12 | 12 | 12
bar | pd | 0.023316 | 0.016321 | 0.023316 | 0.018613 | 0.023316 | 0.023316 | 0.023316 |  |  | 0.023316 | 0.034699 | 0.044746 | 0.044746 | 0.044746 | 0.044746 | 0.02282 | 0.030551 | 0.02494 | 0.030551 |  | 0.030551 | 0.02282 | 0.0052888 | 0.014005 | 0.014005 | 0.014005
% | RV | 70% | 100% | 70% | 100% | 70% | 70% | 70% |  |  | 70% | 47.04% | 36.47% | 36.47% | 51% | 51% | 100% | 74.7% | 100% | 74.7% |  | 74.7% | 100% | 431.5% | 100% | 100% | 100%
kg/kg | x | 0.010189 | 0.010189 | 0.010189 | 0.011647 | 0.010189 | 0.010189 | 0.010189 |  |  | 0.010189 | 0.010189 | 0.010189 | 0.010189 | 0.01434 | 0.01434 | 0.01434 | 0.01434 | 0.015706 | 0.01434 |  | 0.01434 | 0.01434 | 0.01434 | 0.0087232 | 0.0087232 | 0.0087232
[5 empty] | 45.9821 | [13 empty] | 61.1137 | [5 empty] | 34.0806
kJ/kg | h | 45.9821 | 40.1867 | 45.9821 | 45.9821 | 45.9821 | 45.9821 | 45.9821 |  |  | 45.9821 | 52.7519 | 57.2663 | 57.2663 | 67.8834 | 67.8834 | 56.1562 | 61.1137 | 61.1137 | 61.1137 |  | 61.1137 | 56.1562 | 34.0806 | 34.0806 | 34.0806 | 34.0806
kg/hr | massaflow | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 |  |  | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 |  | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
m3/hr | volumeflow | 844.4373 | 828.1579 | 844.4373 | 835.998 | 844.4373 | 844.4373 | 844.4373 |  |  | 844.4373 | 863.4491 | 876.1235 | 876.1235 | 881.8743 | 881.8743 | 848.9734 | 862.8839 | 793.6895 | 862.8839 |  | 862.8839 | 848.9734 | 786.9983 | 815.2087 | 815.2087 | 819.4886
kW | vermogen |  |  |  |  | 0 | 0 | 0 |  |  |  | 1.8805 | 1.254 | 0 | [5 empty] | -1.8805 | [6 empty] | -7.5092
kg/hr | ontvochtig |  |  |  |  | 0 | 0 |  | 0 | kg/hr ontvochtiging | [9 empty] | 0 | [6 empty] | -5.6172
| t hulp |  | 14.3485 |  | 16.4029 | [11 empty] | 19.6528 |  | 21.0948 |  |  |  | 19.6528 |  | 12
xoud
h oud
| pd oud |  | 0.016319 |  | 0.018613 | [11 empty] | 0.02282 |  | 0.02494 |  |  |  | 0.02282 |  | 0.014005
| cpl | 1.0064 | 1.0063 | 1.0064 | 1.0064 | 1.0064 | 1.0064 | 1.0064 |  |  | 1.0064 | 1.0065 | 1.0066 | 1.0066 | 1.0066 | 1.0066 | 1.0064 | 1.0065 | 1.0064 | 1.0065 |  | 1.0065 | 1.0064 | 1.0061 | 1.0063 | 1.0063 | 1.0063
| cpd | 1.8414 | 1.8401 | 1.8414 | 1.8406 | 1.8414 | 1.8414 | 1.8414 |  |  | 1.8414 | 1.8429 | 1.8439 | 1.8439 | 1.8439 | 1.8439 | 1.8413 | 1.8424 | 1.8417 | 1.8424 |  | 1.8424 | 1.8413 | 1.8365 | 1.8396 | 1.8396 | 1.8396
pd
hw
| ro | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 |  |  | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5
hds
hdnat
xs
| rho | 1.1963 | 1.2198 | 1.1963 | 1.2101 | 1.1963 | 1.1963 | 1.1963 |  |  | 1.1963 | 1.1699 | 1.153 | 1.153 | 1.1502 | 1.1502 | 1.1948 | 1.1755 | 1.2797 | 1.1755 |  | 1.1755 | 1.1948 | 1.2889 | 1.2374 | 1.2309 | 1.2309
uit zeller boekje pagina 3
| temp celsius | 20 | 14.3483 | 20 | 16.4029 | 20 | 20 | 20 |  |  | 20 | 26.6 | 31 | 31 | 31 | 31 | 19.6528 | 24.4504 | 21.0948 | 24.4504 |  | 24.4504 | 19.6528 | -1.7218 | 12 | 12 | 12
spec warmtecapaciteit droge lucht | cpl | 1.0064 | 1.0063 | 1.0064 | 1.0064 | 1.0064 | 1.0064 | 1.0064 |  |  | 1.0064 | 1.0065 | 1.0066 | 1.0066 | 1.0066 | 1.0066 | 1.0064 | 1.0065 | 1.0064 | 1.0065 |  | 1.0065 | 1.0064 | 1.0061 | 1.0063 | 1.0063 | 1.0063
spec warmtecapaciteit waterdamp | cpd | 1.8414 | 1.8401 | 1.8414 | 1.8406 | 1.8414 | 1.8414 | 1.8414 |  |  | 1.8414 | 1.8429 | 1.8439 | 1.8439 | 1.8439 | 1.8439 | 1.8413 | 1.8424 | 1.8417 | 1.8424 |  | 1.8424 | 1.8413 | 1.8365 | 1.8396 | 1.8396 | 1.8396
dampdruk waterdamp | pd | 0.023316 | 0.016319 | 0.023316 | 0.018613 | 0.023316 | 0.023316 | 0.023316 |  |  | 0.023316 | 0.034699 | 0.044746 | 0.044746 | 0.044746 | 0.044746 | 0.02282 | 0.030551 | 0.02494 | 0.030551 |  | 0.030551 | 0.02282 | 0.0052888 | 0.014005 | 0.014005 | 0.014005
| T | 293.15 | 287.4983 | 293.15 | 289.5529 | 293.15 | 293.15 | 293.15 |  |  | 293.15 | 299.75 | 304.15 | 304.15 | 304.15 | 304.15 | 292.8028 | 297.6004 | 294.2448 | 297.6004 |  | 297.6004 | 292.8028 | 271.4282 | 285.15 | 285.15 | 285.15
| T2 | 85936.9225 | 82655.2716 | 85936.9225 | 83840.8789 | 85936.9225 | 85936.9225 | 85936.9225 |  |  | 85936.9225 | 89850.0625 | 92507.2225 | 92507.2225 | 92507.2225 | 92507.2225 | 85733.4809 | 88566.0059 | 86580.03 | 88566.0059 |  | 88566.0059 | 85733.4809 | 73673.2603 | 81310.5225 | 81310.5225 | 81310.5225
| A | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 |  |  | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 |  | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151
| B | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 |  |  | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 |  | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726
| c | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 |  |  | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 |  | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625
| teta | 0.0018368 | 0.0018862 | 0.0018368 | 0.001868 | 0.0018368 | 0.0018368 | 0.0018368 |  |  | 0.0018368 | 0.0017819 | 0.0017467 | 0.0017467 | 0.0017467 | 0.0017467 | 0.0018398 | 0.0017995 | 0.0018275 | 0.0017995 |  | 0.0017995 | 0.0018398 | 0.0020392 | 0.0019073 | 0.0019073 | 0.0019073
| D | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 |  |  | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 |  | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42
| E | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 |  |  | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 |  | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414
| F | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 |  |  | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 |  | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979
| <0 tau | -1.5411 | -1.7218 | -1.5411 | -1.6553 | -1.5411 | -1.5411 | -1.5411 |  |  | -1.5411 | -1.3388 | -1.2089 | -1.2089 | -1.2089 | -1.2089 | -1.552 | -1.4037 | -1.5069 | -1.4037 |  | -1.4037 | -1.552 | -2.2766 | -1.7989 | -1.7989 | -1.7989
| 10^ | 0.028768 | 0.018978 | 0.028768 | 0.022118 | 0.028768 | 0.028768 | 0.028768 |  |  | 0.028768 | 0.045832 | 0.061811 | 0.061811 | 0.061811 | 0.061811 | 0.028055 | 0.039472 | 0.031124 | 0.039472 |  | 0.039472 | 0.028055 | 0.0052888 | 0.015888 | 0.015888 | 0.015888
| G | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 |  |  | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 |  | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047
| H | -3177 | -3177 | -3177 | -3177 | -3177 | -3177 | -3177 |  |  | -3177 | -3177 | -3177 | -3177 | -3177 | -3177 | -3177 | -3177 | -3177 | -3177 |  | -3177 | -3177 | -3177 | -3177 | -3177 | -3177
| K | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 |  |  | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 |  | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703
| >0 tau | -1.6324 | -1.7873 | -1.6324 | -1.7302 | -1.6324 | -1.6324 | -1.6324 |  |  | -1.6324 | -1.4597 | -1.3492 | -1.3492 | -1.3492 | -1.3492 | -1.6417 | -1.515 | -1.6031 | -1.515 |  | -1.515 | -1.6417 | -2.2676 | -1.8537 | -1.8537 | -1.8537
| 10^ | 0.023316 | 0.016319 | 0.023316 | 0.018613 | 0.023316 | 0.023316 | 0.023316 |  |  | 0.023316 | 0.034699 | 0.044746 | 0.044746 | 0.044746 | 0.044746 | 0.02282 | 0.030551 | 0.02494 | 0.030551 |  | 0.030551 | 0.02282 | 0.0053998 | 0.014005 | 0.014005 | 0.014005
enthalpie van water | hw | 83.0652 | 59.6003 | 83.0652 | 68.1227 | 83.0652 | 83.0652 | 83.0652 |  |  | 83.0652 | 110.5478 | 128.9118 | 128.9118 | 128.9118 | 128.9118 | 81.6218 | 101.5881 | 87.6185 | 101.5881 |  | 101.5881 | 81.6218 | -6.6906 | 49.8713 | 49.8713 | 49.8713
verdampingswarmte van waterdamp | r | 2453.9877 | 2467.1999 | 2453.9877 | 2462.4076 | 2453.9877 | 2453.9877 | 2453.9877 |  |  | 2453.9877 | 2438.4395 | 2428.0018 | 2428.0018 | 2428.0018 | 2428.0018 | 2454.8021 | 2443.5177 | 2451.4174 | 2443.5177 |  | 2443.5177 | 2454.8021 | 2504.2586 | 2472.6621 | 2472.6621 | 2472.6621
enthalpie van waterdamp op verz.lijn | hd | 2537.0529 | 2526.8001 | 2537.0529 | 2530.5303 | 2537.0529 | 2537.0529 | 2537.0529 |  |  | 2537.0529 | 2548.9874 | 2556.9136 | 2556.9136 | 2556.9136 | 2556.9136 | 2536.4239 | 2545.1058 | 2539.0359 | 2545.1058 |  | 2545.1058 | 2536.4239 | 2497.568 | 2522.5335 | 2522.5335 | 2522.5335
xd
enthalpie van waterdamp in het natdampgebied | hd | 83.0652 | 59.6003 | 83.0652 | 68.1227 | 83.0652 | 83.0652 | 83.0652 |  |  | 83.0652 | 110.5478 | 128.9118 | 128.9118 | 128.9118 | 128.9118 | 81.6218 | 101.5881 | 87.6185 | 101.5881 |  | 101.5881 | 81.6218 | -6.6906 | 49.8713 | 49.8713 | 49.8713
1
2
3
4
5
7
6
8
6a
6b
9

## ontv.buitenlucht (hidden)
Ontvochtigen buitenlucht
zoals Menerga in optie 5 ontvochtigen op warme dagen
datum 13mrt 2004
| flow | 1000 | kg/hr | flow inblaas | 864.8223 | m3/h
| luchtdruk | 1.013 | bar
| rendement 1 | 60 | % | ontvochtiging | 8.9335 | kg/h
| rendement 2 | 0 | %
|  | Ontvochtigen van de buitenlucht | [8 empty] | Hemmes systeem 2e warmtewisselaar
deze warmtewisselaar is op nul rendement gezet
|  | aanzuig | dauwpunt | voor verd | afblaas | werkelijke afbl | gekoeld | uitwtw |  |  |  | toevoer | naverw | naverw | retour | retour bev | dauwpunt | afblaas | afblaas | werkelijke afbl
|  | t1 |  | geen 100% | verz.lijn | t2 | t3 | t4 |  |  | t5 | t6 | t6a | t6b |  | t7 |  | geen 100% | verz.lijn | t8
celsius | t | 20 | 14.3485 | 11.0793 | 13.085 | 13.085 | 5 | 14 |  |  | 14 | 14 | 31 | 31 | 31 | 31 | 19.6528 | 31 | 22.9351 | 31
bar | pd | 0.023316 | 0.016321 | 0.01318 | 0.015036 | 0.015036 | 0.0087266 | 0.015956 |  |  | 0.015956 | 0.015956 | 0.044746 | 0.044746 | 0.044746 | 0.044746 | 0.02282 | 0.044746 | 0.027893 | 0.044746
% | RV | 70% | 100% | 123.8% | 100% | 100% | 100% | 54.69% |  |  | 54.69% | 54.69% | 19.5% | 19.5% | 51% | 0.51 | 100% | 51% | 100% | 51%
kg/kg | x | 0.010189 | 0.010189 | 0.010189 | 0.0093748 | 0.0093748 | 0.0054069 | 0.0054069 |  |  | 0.0054069 | 0.0054069 | 0.0054069 | 0.0054069 | 0.01434 | 0.01434 | 0.01434 | 0.01434 | 0.017619 | 0.01434
[5 empty] | 36.835 | [13 empty] | 67.8834
kJ/kg | h | 45.9821 | 40.1867 | 36.835 | 36.835 | 36.835 | 18.6007 | 27.7479 |  |  | 27.7479 | 27.7479 | 45.0345 | 45.0345 | 67.8834 | 67.8834 | 56.1562 | 67.8834 | 67.8834 | 67.8834
kg/hr | massaflow | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 |  |  | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
m3/hr | volumeflow | 844.4373 | 828.1579 | 818.7406 | 823.4563 | 823.4563 | 795.17 | 820.899 |  |  | 820.899 | 820.899 | 869.4983 | 869.4983 | 881.8743 | 881.8743 | 848.9734 | 881.8743 | 862.9113 | 881.8743
kW | vermogen |  |  |  |  | -2.5409 | -5.0651 | 2.5409 |  |  |  | 0 | 4.8018 | 0 | [5 empty] | 0
kg/hr | ontvochtig |  |  |  |  | -0.81454 | -3.9679 |  | -4.7824 | kg/hr ontvochtiging | [9 empty] | 0
| t hulp |  | 14.3485 |  | 13.085 | [11 empty] | 19.6528 |  | 22.9351
xoud
h oud
| pd oud |  | 0.016319 |  | 0.015036 | [11 empty] | 0.02282 |  | 0.027893
| cpl | 1.0064 | 1.0063 | 1.0063 | 1.0063 | 1.0063 | 1.0062 | 1.0063 |  |  | 1.0063 | 1.0063 | 1.0066 | 1.0066 | 1.0066 | 1.0066 | 1.0064 | 1.0066 | 1.0065 | 1.0066
| cpd | 1.8414 | 1.8401 | 1.8394 | 1.8398 | 1.8398 | 1.838 | 1.84 |  |  | 1.84 | 1.84 | 1.8439 | 1.8439 | 1.8439 | 1.8439 | 1.8413 | 1.8439 | 1.8421 | 1.8439
pd
hw
| ro | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 |  |  | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5 | 2500.5
hds
hdnat
xs
| rho | 1.1963 | 1.2198 | 1.2338 | 1.2258 | 1.2258 | 1.2644 | 1.2248 |  |  | 1.2248 | 1.2248 | 1.1563 | 1.1563 | 1.1502 | 1.1502 | 1.1948 | 1.1502 | 1.1793 | 1.1502
uit zeller boekje pagina 3
| temp celsius | 20 | 14.3483 | 11.0793 | 13.085 | 13.085 | 5 | 14 |  |  | 14 | 14 | 31 | 31 | 31 | 31 | 19.6528 | 31 | 22.9351 | 31
spec warmtecapaciteit droge lucht | cpl | 1.0064 | 1.0063 | 1.0063 | 1.0063 | 1.0063 | 1.0062 | 1.0063 |  |  | 1.0063 | 1.0063 | 1.0066 | 1.0066 | 1.0066 | 1.0066 | 1.0064 | 1.0066 | 1.0065 | 1.0066
spec warmtecapaciteit waterdamp | cpd | 1.8414 | 1.8401 | 1.8394 | 1.8398 | 1.8398 | 1.838 | 1.84 |  |  | 1.84 | 1.84 | 1.8439 | 1.8439 | 1.8439 | 1.8439 | 1.8413 | 1.8439 | 1.8421 | 1.8439
dampdruk waterdamp | pd | 0.023316 | 0.016319 | 0.01318 | 0.015036 | 0.015036 | 0.0087266 | 0.015956 |  |  | 0.015956 | 0.015956 | 0.044746 | 0.044746 | 0.044746 | 0.044746 | 0.02282 | 0.044746 | 0.027893 | 0.044746
| T | 293.15 | 287.4983 | 284.2293 | 286.235 | 286.235 | 278.15 | 287.15 |  |  | 287.15 | 287.15 | 304.15 | 304.15 | 304.15 | 304.15 | 292.8028 | 304.15 | 296.0851 | 304.15
| T2 | 85936.9225 | 82655.2716 | 80786.272 | 81930.4719 | 81930.472 | 77367.4225 | 82455.1225 |  |  | 82455.1225 | 82455.1225 | 92507.2225 | 92507.2225 | 92507.2225 | 92507.2225 | 85733.4809 | 92507.2225 | 87666.3764 | 92507.2225
| A | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 |  |  | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151 | 7.9151
| B | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 |  |  | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726 | 2.6726
| c | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 |  |  | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625 | 0.8625
| teta | 0.0018368 | 0.0018862 | 0.0019157 | 0.0018975 | 0.0018975 | 0.0019728 | 0.0018893 |  |  | 0.0018893 | 0.0018893 | 0.0017467 | 0.0017467 | 0.0017467 | 0.0017467 | 0.0018398 | 0.0017467 | 0.001812 | 0.0017467
| D | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 |  |  | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42 | 176915.42
| E | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 |  |  | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414 | -4320.414
| F | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 |  |  | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979 | 5.7979
| <0 tau | -1.5411 | -1.7218 | -1.8296 | -1.7631 | -1.7631 | -2.0368 | -1.7331 |  |  | -1.7331 | -1.7331 | -1.2089 | -1.2089 | -1.2089 | -1.2089 | -1.552 | -1.2089 | -1.45 | -1.2089
| 10^ | 0.028768 | 0.018978 | 0.014806 | 0.017254 | 0.017254 | 0.0091883 | 0.018488 |  |  | 0.018488 | 0.018488 | 0.061811 | 0.061811 | 0.061811 | 0.061811 | 0.028055 | 0.061811 | 0.03548 | 0.061811
| G | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 |  |  | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047 | 9764.8047
| H | -3177 | -3177 | -3177 | -3177 | -3177 | -3177 | -3177 |  |  | -3177 | -3177 | -3177 | -3177 | -3177 | -3177 | -3177 | -3177 | -3177 | -3177
| K | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 |  |  | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703 | 4.1703
| >0 tau | -1.6324 | -1.7873 | -1.8801 | -1.8229 | -1.8229 | -2.0592 | -1.7971 |  |  | -1.7971 | -1.7971 | -1.3492 | -1.3492 | -1.3492 | -1.3492 | -1.6417 | -1.3492 | -1.5545 | -1.3492
| 10^ | 0.023316 | 0.016319 | 0.01318 | 0.015036 | 0.015036 | 0.0087266 | 0.015956 |  |  | 0.015956 | 0.015956 | 0.044746 | 0.044746 | 0.044746 | 0.044746 | 0.02282 | 0.044746 | 0.027893 | 0.044746
enthalpie van water | hw | 83.0652 | 59.6003 | 46.0603 | 54.3648 | 54.3648 | 20.9517 | 58.1565 |  |  | 58.1565 | 58.1565 | 128.9118 | 128.9118 | 128.9118 | 128.9118 | 81.6218 | 128.9118 | 95.277 | 128.9118
verdampingswarmte van waterdamp | r | 2453.9877 | 2467.1999 | 2474.7994 | 2470.1404 | 2470.1404 | 2488.8492 | 2468.0111 |  |  | 2468.0111 | 2468.0111 | 2428.0018 | 2428.0018 | 2428.0018 | 2428.0018 | 2454.8021 | 2428.0018 | 2447.0892 | 2428.0018
enthalpie van waterdamp op verz.lijn | hd | 2537.0529 | 2526.8001 | 2520.8598 | 2524.5052 | 2524.5052 | 2509.8009 | 2526.1675 |  |  | 2526.1675 | 2526.1675 | 2556.9136 | 2556.9136 | 2556.9136 | 2556.9136 | 2536.4239 | 2556.9136 | 2542.3662 | 2556.9136
xd
enthalpie van waterdamp in het natdampgebied | hd | 83.0652 | 59.6003 | 46.0603 | 54.3648 | 54.3648 | 20.9517 | 58.1565 |  |  | 58.1565 | 58.1565 | 128.9118 | 128.9118 | 128.9118 | 128.9118 | 81.6218 | 128.9118 | 95.277 | 128.9118
1
2
3
4
5
7
6
8
6a
6b
9

## versiebeheer (hidden)
datum | Opmerkingen: | Aanpassing | Doorgevoerd in
2004-03-30 | voor versturen sheets beveiligen | sheets beveiligd en bladen verborgen | ontvochtiger L16 =versie L1.16
2004-03-15 | er zou het echte koeltraject in moeten met opgave van de koelmiddeltemperatuur, dan kan ie met rv ongelijk 100 uit koeler komen en dit kan gunstiger uitpakken voor de nakoeler die dan meer latent dan voelbaar koelt.
2004-03-15 | indien afblaaskoeler op zelfde temp als afblaas ofwel geen koeling dan slaat ie op hol
2004-03-15 | cop curve toepassen voor koeltraject
2004-03-12 |  | plaatjes toegevoegd, gridlines weg | ontvochtiger 16= versie 1.16